## Slide 1
TESTING THE FIELD WINDINGS OF LARGE ELECTRICITY GENERATORS USING THE RSO TEST METHOD.
5. INTERPRETING THE RSO TEST RESULTS
ROWTEST LTD.

## Slide 2
INTERPRETING THE RESULTS FROM RSO TESTS
WHAT TO EXPECT - SOME TYPICAL TEST RESULTS
A number of example RSO waveforms obtained from test results on real and simulated rotor windings are shown in the following slides, with comments where appropriate.
All of the test results were obtained using the TDR200 unit in its Digital operating mode.

## Slide 3
FAULT-FREE ROTOR WINDING - INPUT ENDS
This and the next slide show typical RSO waveforms at the input and output ends of a large fault-free 660MW rotor. These waveforms were obtained by optimising the input and out end impedance matching resistors and the pulse and display widths as described in the instruction manuals.
Input end waveforms for a fault-free rotor winding
There are two identical and superimposed waveforms (red and blue) corresponding to the pulses injected at each end of the winding. These waveforms are compared and used to view and detect any winding faults.
Note the two identical end1 (red) and end 2 (blue) waveforms and the horizontal (green) difference waveform.
These are the RSO results which should be obtained for a healthy rotor winding.
Input ends

## Slide 4
FAULT-FREE ROTOR WINDING - OUTPUT ENDS
Output end waveforms
This figure shows the waveforms at the output ends of the winding.
The cursor button has been used to measure the single-pass transit time* for the RSO pulse to travel from one end of the winding to the other end) for fault location purposes.
* In this case 24.8uS
Output ends

## Slide 5
RSO WAVEFORMS FOR TYPICAL WINDING FAULTS
The results given in the following sheets were obtained by applying winding faults to a large 2-pole 660 MW rotor which had been removed from the generator for maintenance.
One end-ring had been removed, which allowed simulated faults to be applied to the half-winding connected to the end 1 slip ring (red waveforms).
If there is a fault in the rotor winding, the red and blue end waveforms will not be identical.
Results are given for inter-turn and earth faults and also for a high-resistance joint.

## Slide 6
FAULT-FREE ROTOR - ONE END RING REMOVED
With one end ring removed, the characteristic impedance of the rotor winding changes at these points in the winding, resulting in a peak in the input end waveforms as shown.
However, note that both the red and blue waveforms remain identical as there is no winding fault.
No fault Input end waveforms
with one end ring removed.

## Slide 7
RSO RESULTS FOR FOR SHORTED TURNS AND EARTH FAULTS
(a) Input end waveforms (b) Input end waveforms
for a shorted turn for an earth fault

## Slide 8
RSO RESULTS FOR FOR A HIGH-RESISTANCE JOINT
Input end waveforms for a simulated high-resistance joint
obtained using a delay line

## Slide 9
ROTOR - ONE END RING REMOVED - SHORTED COIL
Shorting out a complete set of windings in a slot coil causes a characteristic loop to appear between the red and blue waveforms.
Note that the applied fault is nearest to the end 1 (red waveform) and that the red end waveform appears to first increase, then decreases at the fault location.
Short circuit applied to
last coil before end of half-winding

## Slide 10
ROTOR - ONE END RING REMOVED - SHORTED TURN IN COIL 1
1 shorted turn applied to first coil from end 1 slip ring
The effect of shorting out a single turn produces a maximum difference in the input end waveforms when the shorted turn is close to the start of the winding.

## Slide 11
ROTOR WINDING WITH SHORTED TURN IN COIL 3
Shorted turn applied to third coil from end 1 slip ring
As the location of the fault is moved towards the centre of the winding, the measurement sensitivity decreases.

## Slide 12
ROTOR WITH SHORTED TURN IN LAST COIL IN HALF-WINDING
Although the measurement sensitivity has further decreased, it is still possible to detect a shorted turn close to the centre of the rotor winding.
Shorted turn applied to last coil
in end 1 half-winding

## Slide 13
EARTH FAULT IN LAST COIL IN HALF-WINDING
Earth fault applied to last coil in
end 1 half-winding
An earth fault is easily detected and located using the RSO test.
In this case, a fault has been applied to the half-winding closest to end 1 (red waveform).

## Slide 14
The Rotor model used for the following tests is a 128 section delay line which simulates a 2-pole cylindrical alternator rotor winding containing two identical (north and south pole) half-windings.
Each half-winding contains 8 "Coils" (slot-pairs), each of which has 8 "turns". So the complete rotor winding contains 2 X 8 X 8 = 128 turns.
The junctions between each delay line section are connected to 2mm white test terminals.
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE

## Slide 15
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Input ends R2 = 100 Ohms
Output ends
NO APPLIED FAULTS

## Slide 16
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
R2 = 200 Ohms
R2 = 50 Ohms
NO APPLIED FAULTS

## Slide 17
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Short between turns 1 and 2 of Coil 1
Short between turns 1 and 2 of Coil 2

## Slide 18
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Short between turns 1 and 2 of Coil 3
Short between turns 1 and 2 of Coil 4

## Slide 19
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Short between turns 1 and 2 of Coil 5
Short between turns 1 and 2 of Coil 6

## Slide 20
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Short between turns 1 and 2 of Coil 7
Short between turns 1 and 2 of Coil 8

## Slide 21
RESULTS OBTAINED USING A 128 SECTION ROTOR MODEL DELAY LINE
Short between turns 7 and 8 of Coil 8
As the location of the fault is moved towards the centre of the winding, the measurement sensitivity decreases.
However, it is still possible to detect a shorted turn close to the centre of the rotor winding

## Slide 22
OTHER CAUSES OF NON-IDENTICAL WAVEFORMS
Apart from these common faults, there are circumstances where, the RSO test may indicate that a good rotor is faulty. Possible causes are:
1. Poor contact between the slip rings and the test leads.
If this occurs, the RSO waveforms will resemble those shown here, the difference between the traces being dependent on the magnitude of the contact resistance. The Red end waveform has the high contact resistance, which has increased the winding impedance at this end.
If this occurs, re-check the contact between the test leads and the slip rings before assuming that the rotor winding is faulty.

## Slide 23
OTHER CAUSES OF NON-IDENTICAL WAVEFORMS
2. Poor contact between the earth lead and the rotor shaft. Again, the cure is to re-check the contact resistance.
3. The characteristic impedances of both rotor half windings are not identical. On the face of it, this seems most improbable. However, it may be caused by a previous repair to one half winding using insulation different from that used during manufacture.
Moreover, when the end rings are removed, the end windings expand radially in a non-uniform manner, causing the impedances to differ. Consequently, two slightly different traces are often obtained when one or both end rings are removed.

## Slide 24
A NOTE ON SHORTED TURNS
The RSO test is very sensitive and will detect shorts between turns which do not carry any significant current.
The winding resistance for a large generator rotor is around 0.1 Ohms (100mΩ). As the rotor winding typically contains around 150 turns, the resistance around a single turn will be less than 1m Ω. Consequently, a short between turns of 1Ω will only carry 0.1% of the rated current. As typical large rotor currents are around 3000A, this will result in a current of only 3A through the short. If the short resistance value is 10 Ω, this current reduces to 0.3A.
The power (heat) dissipated at the short is calculated using P = I2 x R where I is the current through the short and R is the short resistance. For a 1Ω/3A short, the power dissipated will be 9 watts, and this amount of heat may be significant enough to burn the insulation. For a 10Ω/0.3A short, the power dissipated will be 0.9 watts, which is unlikely to cause any problems on a large rotor winding.
If a shorted turn is detected by an RSO test, further tests will normally be required to determine whether the short is severe enough to carry significant current. A suitable method is to use a magnetic flux probe (search coil) which will only detect current-carrying shorted turns.

## Slide 25
TEST CONDITIONS
For complete confidence in the integrity of a rotor winding, the RSO test should ideally be carried out with the rotor both at rest and at speed, because even if no winding faults are found on a stationary rotor, faults may still develop at speed. It is therefore prudent to test all rotors at speed as well as at rest if possible, to ensure the rotor is completely free from winding faults.
In a perfect world, the RSO test waveforms will indicate that the rotor winding is fault-free (identical red and blue traces). However if this is not the case, careful consideration needs to be given to what, if any remedial action is taken.
In general, the outcome will depend on whether the test has been carried out in a manufacturer or repairer’s works or whether the test is conducted in a Power Generation plant.

## Slide 26
TESTS WHILE UNDER CONSTRUCTION OR REPAIR
One of the major advantages of the RSO technique is that it is a low-voltage test method and can be safely left running on a rotor winding while it is under repair. Consequently, it is particularly valuable when carried out in the premises of a manufacturer or repairer because any winding faults that are found can be quickly located and remedied. Moreover, many Plant Operators insist on witnessing RSO tests at manufacturers' premises before agreeing to take delivery of new or repaired rotors.
TESTS DURING SERVICE
In contrast, if a winding fault is detected on a rotor in service at a Power Utility company, the choices are more complex, because of the cost of lost generation as well as the cost and complexity of any repair work. It has been reported* that as many as 50% of all rotors tested using the RSO test show evidence of winding faults.
*

## Slide 27
RECOMMENDED ACTIONS FOR PLANT OPERATORS *
When the RSO test was first used routinely in the UK (from around 1980 onwards), many rotors were found to have winding faults, and these included some brand new rotors. However as manufacturers started to use the RSO test themselves, the number of new rotors delivered with winding faults rapidly reduced to zero. In current practice, it is reasonable for plant operators to expect that any new rotor will be delivered free from any winding faults.
However, the situation for rotors currently in service is more complicated if the RSO test indicates winding faults. Symptoms which can be caused by shorted turns in large generators include increased vibration levels, thermal damage to the winding insulation and the need for increased excitation current for a given power output. If inter-turn faults detected by an RSO test are not causing any obvious operational problems, many plant operators will decide to continue to run the generator, while monitoring it regularly to determine whether the fault is stable or whether it is changing and/or worsening.
* See disclaimer in Instruction Manual

## Slide 28
RECOMMENDED ACTIONS FOR PLANT OPERATORS *
If operational problems are being experienced, a flux-probe (search coil waveform) test can be carried out if a suitable search coil has been previously installed in the generator air-gap. This will determine whether the winding fault is current-carrying.
Comparison of the RSO waveforms between results obtained for similar rotors at the same generation site can also be helpful in making decisions for further action.
If an earth fault is detected by the RSO test, it is likely that this will have already been detected by other on-line monitoring equipment. Most plant operators are reluctant to run a large generator with a single earth fault, as major damage can occur if a second earth fault occurs, because this may short out much of the rotor winding.
* See disclaimer in Instruction Manual

## Slide 29
Thank you for viewing this presentation.
If you have any questions, please send them to us at
enquiries@rowtest .com.
We will try to respond to you as soon as we can.