## Slide 1
TESTING THE FIELD WINDINGS OF LARGE ELECTRICITY GENERATORS USING THE RSO TEST METHOD.
6. USING THE TDR200 IN ANALOGUE MODE
ROWTEST LTD.

## Slide 2
OPERATION IN ANALOGUE MODE
The TDR200 Rotor Reflectometer is normally used in its preferred Digital Mode with a Control PC.
However, it can also be used in an alternative Analogue Mode with an oscilloscope, in a similar way to the previous TDR100 model.
In this case, the RSO waveforms are displayed on an oscilloscope screen.
The operation in analogue mode is described in this presentation based on the use of the supplied DL100 delay line.
The equipment should be set up as shown in the following slides.
Note that an analogue (or digital) oscilloscope (not supplied) will be required.

## Slide 3
SETTING UP THE EQUIPMENT
1. Connect the delay line to the TDR100 using the short 3-core connecting lead supplied. Ensure that the delay line patch lead (white lead with yellow plugs) is disconnected from the delay line terminals.
2. Connect the Reflectometer to the oscilloscope input terminals using the coaxial leads supplied.
3. Connect the mains lead to the mains supply and the rear panel connector.
The connection arrangements are shown in the following 2 slides.

## Slide 4
CONNECTION DIAGRAM IN ANALOGUE MODE

## Slide 5
PHYSICAL REALISATION

## Slide 6
R1= R2 = :100
PULSE FREQUENCY : Fully clockwise
PULSE WIDTH SWITCH : Centre position
PULSE WIDTH POTENTIOMETER : Mid scale
OUTPUT MODE SWITCH : Auto
R1/R2 TOGGLE SWITCH : Up (0 - 500 Ohms)
SETTING THE TDR200 FRONT PANEL CONTROLS
The front panel controls on the Reflectometer should be set initially as shown below:

## Slide 7
SETTING THE OSCILLOSCOPE CONTROLS
In analogue mode, the best results will be obtained using a conventional analogue oscilloscope, as this allows each pair of RSO waveforms to be displayed and viewed in real time. A basic digital camera can be used to capture the screen shots for permanent records.
Set the oscilloscope controls initially as follows:
DISPLAY : Channel 1
VERTICAL SENSITIVITY: 1V/CM (Both channels)
TRIGGER CONTROLS
MODE: Normal
SOURCE: Channel 1
LEVEL: Positive
SLOPE: Positive
COUPLING: D.C.
TIME BASE: 5 sec/division

## Slide 8
SWITCH ON THE EQUIPMENT
Switch on the Reflectometer (mains switch on rear panel and rocker switch on front panel). The red and green LEDs on the front panel should light.
Switch on the oscilloscope and adjust the controls until a waveform similar to that shown in the next slide is displayed.
Note that operation of the rear panel switch charges the internal battery and lights the green Charging LED, while that on the front panel switches on the unit and lights the red Power LED.

## Slide 9
Input end waveforms
With the oscilloscope monitoring the input ends of the delay line, adjust the pulse width so that the display resembles that shown in the figure.
Under these conditions, R1 and R2 match the characteristic impedance of the delay line and the pulses pass through the delay line and are absorbed without reflection in R2.
The sharp waveform dip is caused by a deliberate impedance mismatch at the ends of the delay line.
TYPICAL OSCILLOSCOPE WAVEFORMS UNDER MATCHED CONDITIONS
Input ends waveforms with R1 = R2 = 100 Ohms

## Slide 10
Output end waveforms
Now set the oscilloscope to monitor the output ends of the delay line and set the time base to 2uS/division.
Ensure that the triggering remains set to the input ends signals and reset R1 = R2 = 100 Ohms.
The output end waveforms should now appear as shown in the figure.
No signal is received at the far end of the delay line until a time delay, known as the single-pass transit time (SPT) of approximately 10uS (4 divisions).
TYPICAL OSCILLOSCOPE WAVEFORMS UNDER MATCHED CONDITIONS
Output ends waveforms with R1 and R2 = 100 Ohms

## Slide 11
SETTING THE IMPEDANCE MATCHING CONTROLS R1 AND R2
The impedance matching controls R1 and R2 have a major effect on the displayed waveforms.
However, the effects are identical for both sets of RSO waveforms and it is impossible to obtain different waveforms for each half-winding of a fault-free rotor winding by incorrect setting of these controls.
The correct values of R1 and R2 for use with the delay line are approximately 100 Ohms. However, for a real rotor winding, this value will be unknown initially and must be measured as described in the following slides.
CHANGING THE VALUE OF R1
The effect of adjusting R1 is primarily to adjust the amplitudes of the displayed RSO waveforms. In practice, R1 is normally set to the same value as R2, once the correct value for R2 has been found, as described next.

## Slide 12
CHANGING THE VALUE OF R2
The effect of mismatching the value of the output end terminating resistor R2 can be demonstrated by changing the setting of R2 on the Reflectometer.
When R2 is set to zero, the output pulses are reflected back to the input ends of the delay line with opposite polarity.
Consequently, the pulse amplitude monitored at the input end of the winding becomes zero after a time delay during which the pulses pass through the delay line and back again.
This delay time is known as the double-pass transit time (DPT).
The figure shows the input end waveforms when R2=0. The double pass transit time is seen to be approximately 20S (4 divisons).

## Slide 13
CHANGING THE VALUE OF R2
Similarly, when the value of R2 is set to a value larger than that of the delay line characteristic impedance, partial reflection of the the pulses again occurs.
But now they are reflected back to the input ends of the delay line with positive polarity.
The pulse amplitude monitored at the input end of the winding therefore increases after the double-pass transit time.
This figure shows the input-end waveforms obtained with R2 set to 150 Ohms.

## Slide 14
In all of the examples listed to-date, the oscilloscope has displayed 2 superimposed waveforms.
To confirm this, push in each of the trace identify buttons in turn. This connects a high value resistor across the selected winding end and displaces one waveform vertically.
This allows the individual waveforms at each end of the winding to be identified.
Operation of trace identification buttons
USING THE TRACE IDENTIFY BUTTONS

## Slide 15
Simulated inter-coil fault
The effect of a shorted turn or coil can be demonstrated by shorting out one or more delay line sections.
The figure shows the RSO input end waveforms when the 2mm patch lead is connected between terminals 4 and 5 on the delay line.
The approximate fault location can be estimated by comparing the time at which the waveforms start to diverge with the double-pass transit time.
Note that a single shorted turn on a real rotor winding will give a much smaller difference between the input end waveforms.
Short applied between terminals 4 and 5 on delay line
DEMONSTRATING WINDING FAULTS WITH THE DL100 DELAY LINE

## Slide 16
Simulated earth fault
The effect of a simulated earth fault may be demonstrated by shorting one of the delay line junctions to earth using the 2mm plug lead supplied.
The figure shows the result of shorting junction 4 to earth.
Short applied between terminals 4 and ground on delay line
DEMONSTRATING WINDING FAULTS WITH THE DL100 DELAY LINE

## Slide 17
INTERPRETING AND RECORDING THE RSO WAVEFORMS
A normal fault-free rotor winding is characterised by 2 identical waveforms at each end of the rotor winding.
Rotor windings containing faults will display non-identical waveforms.
The simplest method to record the RSO test results in analogue mode is to photograph the oscilloscope screen using a digital camera (as used for the photos in this presentation.
Detailed information about the RSO test and practical advice on using this test method on real rotor windings can be found in other presentations in this series and also in the Instruction manuals supplied with the equipment.
Further information can be found in a number of technical papers included in the supplied documentation CD.

## Slide 18
Thank you for viewing this presentation.
If you have any questions, please send them to us at
enquiries@rowtest .com.
We will try to respond to you as soon as we can.