## Slide 1
TESTING THE FIELD WINDINGS OF LARGE ELECTRICITY GENERATORS USING THE RSO METHOD.
2. AN INTRODUCTION TO THE RSO TEST
ROWTEST LTD.

## Slide 2
INTRODUCTION TO THE RSO TEST
The RSO (Recurrent Surge Oscillograph) test was developed to detect and locate faults in the field windings of large turbo-alternator rotor windings.
It uses a modified form of time domain reflectometry (TDR) to apply a D.C. voltage step (or pulse) between each end of the rotor winding and the rotor body in turn. The resulting waveforms are monitored and compared, allowing any winding faults (particularly inter-turn faults) to be detected and located.
The test was invented by A.E Grant of the UK Central Electricity Board (CEGB) in 1971. Some useful practical information about the RSO test is contained in the following conference paper, from which some content in this presentation (including the comments in the next 2 slides) has been copied with permission:

## Slide 5
WHAT IS THE RSO TEST USED FOR?
Testing the windings of turbogenerator rotors to detect and locate:
Short-circuits between turns (shorted turns).
Short-circuits to ground (earth faults)
High-resistance joints.
The test relies on 2 basic principles:

## Slide 6
All cylindrical rotor windings are symmetrical when viewed from each end of the winding. For example, a 2-pole rotor contains two nominally-identical half-windings, one for the North pole and the other for the South pole, both of which are connected in series. A four pole rotor is similarly symmetrical.
Representation of a 2-pole rotor winding showing the identical North and South pole half-windings
PRINCIPLE 1. SYMMETRY PROPERTIES

## Slide 7
Cylindrical rotor windings can be approximated as electrical transmission lines, which have an overall characteristic or wave impedance (similar to that of a coaxial cable)
This occurs because the field conductors of the rotor winding sit largely within enclosed metal slots in the rotor forging. Consequently, if an electrical pulse is applied between one end of the winding and the rotor body, it will travel through the winding to the far end where it will emerge after a finite time delay.
The RSO test method uses transmission line measurement techniques, as described later, to identify (and locate approximately) any faults in the rotor winding.
Winding faults will cause the wave impedance to decrease at the fault location. This changes the shape of the RSO waveforms, allowing the fault to be identified and its approximate location found.
PRINCIPLE 2. TRANSMISSION LINE APPROXIMATION

## Slide 8
These symmetry and transmission line properties are used to compare the response of the rotor winding to voltage pulses applied in turn between each slip-ring (or winding end) and the rotor body.
Although the applied RSO pulse is often has a good rectangular waveform, the electrical properties of the rotor winding modify the pulses as they pass through the winding. The resulting modified pulse waveforms are monitored at both (input and output) ends of the rotor winding and appear as shown below for a typical fault-free rotor winding.
RSO TEST FUNDAMENTALS
Input end RSO waveforms
Output end RSO waveforms

## Slide 9
The RSO pulses are applied at each end (slip ring) of the winding in turn and the resulting 2 input end waveforms are compared. In the Rowtest TDR100 and TRD200 RSO test systems, this is done automatically, allowing the waveforms at the INPUT ENDS of the winding to be superimposed for viewing in real-time.
The (pair of) RSO pulse waveforms at the remote (OUTPUT) end of the winding are used to measure the time taken for the pulse to travel from the INPUT end to the OUTPUT end. This transit time is used as a reference value in the calculation to find the approximate location of any winding faults as shown later.
The pairs of superimposed RSO pulse waveforms at the INPUT ends of the winding are complex waveforms, caused by multiple reflections which occur every time there is a change in the wave impedance of the rotor winding (including those caused by winding faults to ground or between turns).
Comparing the pair of superimposed input end waveforms allows any winding faults to be detected and located
RSO TEST FUNDAMENTALS

## Slide 10
If the rotor winding is fault-free, two identical waveforms will be observed for the input end pulses injected at each slip ring. However, if one half-winding contains a fault, the two input end waveforms will differ.
It should be noted that even for a fault-free winding, there will be multiple reflections within the rotor winding at each change in wave impedance.
This occurs primarily between the long sections of conductors inside the radial slots and the shorter sections in the cross-over end regions, where the wave impedance is higher. The result is complex RSO waveforms which are difficult to interpret in isolation .
However, the rotor symmetry property ensures that the 2 waveforms monitored at the input ends of the winding will always be identical for a fault-free rotor under normal test conditions.
However, if the superimposed input end waveforms are not identical, the likely cause is a fault in the winding.
RSO TEST FUNDAMENTALS

## Slide 11
The RSO (Recurrent Surge Oscillograph) test was developed to detect and locate faults in the field windings of large turbo-alternator rotor windings. It uses a modified form of time domain reflectometry to apply D.C. voltage step (or pulse) between one end of the rotor winding and the rotor body and monitoring and comparing the resultant waveforms. It was first described in a paper by A.E Grant in 1971.
Grant used a square pulse train generated by a simple electronic circuit and the Rowtest Reflectometer is based on this concept.
Some other suppliers (eg Sumatron) use a short pulse which is injected at both ends of the winding simultaneously. The principle of operation of both methods is similar, but the resulting RSO waveforms look very different.
HISTORY OF THE RSO TEST

## Slide 13
Grant’s RSO Pulse Generator

## Slide 14
Connections to Rotor

## Slide 15
A low-voltage pulse (12V) is applied between one of the rotor slip rings and ground and the transmitted pulse received at the remote end of the rotor (C2) and the reflected pulse at the sending end (C1) are monitored as shown below.
A pair of adjustable resistors (RV1 and RV2) are set to match the pulse generator and terminating resistor to the wave impedance of the rotor winding (typically in the range 30 - 1000 Ohms). This ensures that the winding is tested under repeatable conditions and minimises multiple reflections of the pulse within the winding.
PRINCIPLE OF OPERATION OF THE RSO TEST (ROWTEST VERSION)

## Slide 16
Typical RSO Oscilloscope waveforms for a fault-free rotor winding
C1 (input ends)
No fault
C2 (output ends)
No fault
C1 (input ends)
Earth fault
C1 (input ends)
Inter-turn fault
RSO WAVEFORMS FOR A FAULT-FREE ROTOR WINDING
The RSO test is carried out by applying pulses from each end of the rotor winding in turn and the RSO waveforms at each end of the winding are recorded and compared. If the rotor is fault-free, the oscilloscope traces will be identical as shown below.

## Slide 17
In practice, the TDR100/200 test instruments apply pulses alternately from each end of the rotor winding via an internal electronic changeover switch as shown above.
Although the TDR200 can be used with an oscilloscope to view the RSO waveforms when operating in its simple Analogue mode, in its normal Digital mode of operation, these waveforms are displayed directly on the screen of a Control PC.
MODIFIED GRANT CIRCUIT USED IN THE TDR200 REFLECTOMETER

## Slide 18
RSO WAVEFORMS FOR FAULTY ROTOR WINDINGS
If there is a fault in the rotor winding, the RSO waveforms measured on the C1 (input ends) channel will resemble those shown below for an earth and interturn fault respectively.
Typical RSO oscilloscope waveforms for rotors with earth and interturn faults
C1 (input ends)
Earth fault
C1 (input ends)
Inter-turn fault

## Slide 19
There are 2 different RSO test methods in common use.
1. The long pulse alternate-end excitation (Grant) method.
This is the method used in the Rowtest TDR200 equipment
2. The short pulse simultaneous excitation method which is used in the Sumatron RSO equipment.
Both methods use the same principle of operation, but display very different RSO waveforms.
For completeness, we have given examples of waveforms using the short pulse method in the following slides and compared them with those obtained using the Rowtest equipment.
RSO TEST METHODS

## Slide 20
SHORT PULSE (SUMATRON) VERSION
Note that in the Sumatron equipment, short pulses are injected from both ends of the winding simultaneously.

## Slide 21
EXAMPLE OF RSO WAVEFORMS USING THE SHORT-PULSE METHOD
SHORT PULSE VERSION
Note that the one of the waveforms has been displaced vertically for clarity.
For each of the blue and yellow waveforms, the first peak corresponds to the pulse injected from one end of the winding and the second peak is caused by that injected from the remote end.

## Slide 22
EXAMPLES OF RSO WAVEFORMS OBTAINED USING THE LONG PULSE METHOD (SHOWING 2 SUPERIMPOSED WAVEFORMS)
Input end RSO waveforms for a fault-free winding
Output end RSO waveforms for a fault-free winding

## Slide 25
TRANSMISSION AND DELAY LINES
In this section we explain how the RSO test uses transmission line measurement techniques to detect and locate faults in rotor windings.
We then show how a simple electrical model of a transmission line can be realised using basic electrical components to construct a delay line which can be used to demonstrate the RSO method without the need for access to a real rotor winding.
The most common example of a transmission line is the coaxial cable which connects the aerial to a television.
Transmission line properties must be considered when the length of a circuit conductor becomes comparable with the wavelength of the applied signal (or its components).

## Slide 26
(UNIVERSITY OF SINGAPORE)
TRANSMISSION LINE PROPAGATION

## Slide 27
(UNIVERSITY OF SINGAPORE)

## Slide 28
The windings of a typical cylindrical rotor are contained within rectangular slots machined radially into the steel rotor forging.
The figure shows the cross-section of a typical radial slot (in this case, containing 7 turns of insulated copper bar)
This rotor winding geometry approximates to a high-frequency transmission line (similar to a coaxial cable), as the conductors sit within an enclosed metal screen formed by the slots in the rotor forging.
This property is used in the RSO test to identify and locate approximately any faults in the rotor winding.
(GE Power Systems)
ROTOR CONDUCTOR CONFIGURATION INSIDE RADIAL SLOTS

## Slide 29
When an electrical pulse is applied between one end of the rotor field winding and the rotor body (ground), it will take a finite time (T1 seconds ) to travel through the winding before it emerges at the far end of the winding.
The pulse travels at a speed which is a fraction of the velocity of light and, T1 is known as the single-pass transit time. For a typical rotor field winding, T1 is a few tens of microseconds.
RSO PULSE PROPAGATION

## Slide 30
C1 (input ends)
Earth fault
C1 (input ends)
Inter-turn fault
These are typical RSO waveforms monitored at the input and output ends of a fault-free rotor winding. Note the distorted output waveform and time delay (T1).
C1 (input ends)
No fault
C2 (output ends)
No fault
INPUT ENDS
OUTPUT ENDS

## Slide 31
The rotor field winding has a number of transmission line properties, including a finite transit time (T1) and also a well-defined wave impedance Z0.
We can therefore approximate the field winding by an equivalent length of transmission line as shown above.
To avoid the need for a real rotor for demonstrating the RSO test, we would prefer to have a portable rotor winding simulator.
However, as the pulse travels near the speed of light (3 x 10^8 m/S), in 1uS it will travel around 300 metres. So to simulate a rotor winding with a transit time of eg 20uS, we would need 300 x 20 = 6000 metres of coaxial cable.
RSO PULSE PROPAGATION

## Slide 32
DELAY LINE APPROXIMATION TO ROTOR WINDING
This would be impractical, but fortunately, a transmission line can be approximated by an equivalent circuit of a series of L/C circuits, known as a delay line.
A simple 10-section delay line of this type is supplied with each TDR200 system.
It has a delay time of 1uS per section (10uS overall) and a wave impedance (Z0) of 100 Ohms
The next few slide shows how a pulse propagates through an ideal transmission line.

## Slide 33
The figure shows how a long pulse travels through an ideal transmission line.
The waveforms viewed at the input ends of the delay line depend on how the output end is terminated.
Note the time delays Td (=T1) and the changes to the input end waveforms after the reflections from the end of the delay line at time 2xTd.

## Slide 34
This slide shows idealised and actual RSO waveforms at the input and output ends of an actual fault-free rotor winding, where the output end is terminated in the wave (impedance of the rotor winding.
Note that there are 2 superimposed RSO waveforms which have been injected from each end of the winding in turn.
Input ends
Output ends

## Slide 35
Short circuit to rotor body at end of 5th coil slot (16 coils in winding)
EFFECT OF AN EARTH FAULT ON THE WINDING IMPEDANCE
If there is a fault in the rotor winding, the wave impedance at this point will decrease and cause part of the pulse to be reflected back to the input ends. This slide shows simplified and actual measured superimposed input end waveforms for a rotor winding with an earth fault.
Simplified RSO input end waveforms for an earth fault

## Slide 36
Measured waveforms for a
rotor winding with a single
shorted turn.
EFFECT OF A SHORTED TURN
The wave impedance of a rotor winding with a shorted turn also decreases at the fault location and the 2 superimposed RSO waveforms form a loop, as the reduction in wave impedance occurs at different times for pulses injected from each end of the winding (unless the fault is in the centre of the winding).

## Slide 37
The reason for the reduction in impedance at a shorted turn can be explained by considering the effect on the incident pulse of a single shorted turn.
At the short location, the injected pulse can travel around one of several possible alternative transmission line paths as shown and the wave impedances of these paths are all in parallel, so reducing the wave impedance at this point.
This will occur first for the pulse injected from the end nearest the short and then again for the pulse injected from the end remote from the fault, so forming a loop in the superimposed waveforms.
EFFECT OF A SHORTED TURN ON WAVE IMPEDANCE

## Slide 38
TDR200 RSO WAVEFORMS FOR DEMONSTRATION DELAY LINE
These effects can be demonstrated using the DL100 delay line. The figures below show the RSO waveforms at the input and ends of the rotor winding for the delay line with no faults applied. These show 2 perfectly-superimposed waveforms.
Input end waveforms Output end waveforms

## Slide 39
SIMULATED WINDING FAULTS APPLIED TO A DELAY LINE
The slides shown here show the input end waveforms when inter-turn and ground faults are applied to the same delay line. The red waveform corresponds to the pulse injected from end 1 of the winding and the blue waveforms to that from end 2. The green waveform is the difference between the red and blue waveforms.
Shorted turn between Earth fault applied to terminals 4 and 5 terminal 4

## Slide 40
EFFECTS OF MIS-MATCHING THE DELAY LINE TERMINATING IMPEDANCE R2
The delay line can also be used to show the effects of mis-matching the terminating impedance R2 at the output ends of the winding as shown below.
R2 = 200 Ohms R2 = 10 Ohms
(R1 = 100 Ohms) (R1 = 100 Ohms)

## Slide 41
LOCATING WINDING FAULTS
The location of a single winding fault can be found (approximately) by noting the time at which the input end RSO waveforms start to diverge and comparing this time with 2 x the time taken to pass from one end of the rotor winding to the remote end.
The first step is to measure the single pass transit time from the waveforms at the output ends at the rotor winding as shown below.
The transit time for the RSO pulse to travel from one end of the winding to the other end is measured as 36.3uS in the output ends waveform plot opposite.

## Slide 42
LOCATING WINDING FAULTS
When the input end waveforms are viewed for this rotor with an inter-turn fault, the superimposed waveforms start to diverge at 23.2 uS from the start of the pulse.
So in this case, the shorted turn occurs approximately
((23.2/(2*36.3))*100 = 32% of the total winding length from the end of the winding connected to the Reflectometer Red terminal.
As this rotor has 16 coils each containing 8 turns, the estimated fault position is in turn 41 ie turn 2 of coil 5 counting from the end connected to the Red terminal.

## Slide 43
If the rotor has been removed from the generator, a further and more precise method for locating interturn faults is possible.
The method is based on applying a similar fault to turns in the fault-free half of the winding and adjusting the position of the applied fault until the 2 input end waveforms are identical (or nearly so).
Further details of this technique, which is particularly useful during a rotor winding repair, are given in the TDR200 Instruction Manuals.
LOCATING WINDING FAULTS

## Slide 44
Thank you for viewing this presentation.
If you have any questions, please send them to us at
enquiries@rowtest .com.
We will try to respond to you as soon as we can.